## LineCode
Id_LineCode | nphases | r1 | x1 | r0 | x0 | C1 | C0 | units | rmatrix | xmatrix | cmatrix | baseFreq | normamps | emergamps | faultrate | pctperm | repair | Kron | Rg | Xg | rho | neutral | B1 | B0 | Seasons | Ratings | LineType | like
1 | 3 | [7 empty] | [0.086666667 ¦0.029545455 0.088371212 ¦0.02907197 0.029924242 0.087405303] | [0.204166667 ¦0.095018939 0.198522727 ¦0.072897727 0.080227273 0.201723485] | [2.851710072 ¦-0.920293787 3.004631862 ¦-0.350755566 -0.585011253 2.71134756] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
2 | 3 | [7 empty] | [0.088371212 ¦0.02992424 0.087405303 ¦0.029545455 0.02907197 0.086666667] | [0.198522727 ¦0.080227273 0.201723485 ¦0.095018939 0.072897727 0.204166667] | [3.004631862 ¦-0.585011253 2.71134756 ¦-0.920293787 -0.350755566 2.851710072] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
3 | 3 | [7 empty] | [0.087405303 ¦0.02907197 0.086666667 ¦0.029924242 0.029545455 0.088371212] | [0.201723485 ¦0.072897727 0.204166667 ¦0.080227273 0.095018939 0.198522727] | [2.71134756 ¦-0.350755566 2.851710072 ¦-0.585011253 -0.920293787 3.004631862] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
4 | 3 | [7 empty] | [0.087405303 ¦0.029924242 0.088371212 ¦0.02907197 0.029545455 0.086666667] | [0.201723485 ¦0.080227273 0.198522727 ¦0.072897727 0.095018939 0.204166667] | [2.71134756 ¦0.585011253 3.004631862 ¦-0.350755566 -0.920293787 2.851710072] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
5 | 3 | [7 empty] | [0.088371212 ¦0.029545455 0.086666667 ¦0.029924242 0.02907197 0.087405303] | [0.198522727 ¦0.095018939 0.204166667 ¦0.080227273 0.072897727 0.201723485] | [3.004631862 ¦-0.920293787 2.851710072 ¦-0.585011253 -0.350755566 2.71134756] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
6 | 3 | [7 empty] | [0.086666667 ¦0.02907197 0.087405303 ¦0.029545455 0.029924242 0.088371212] | [0.204166667 ¦0.072897727 0.201723485 ¦0.095018939 0.080227273 0.198522727] | [2.851710072 ¦-0.350755566 2.71134756 ¦-0.920293787 -0.585011253 3.004631862] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
7 | 2 | [7 empty] | [0.086666667 ¦0.02907197 0.087405303] | [0.204166667 ¦0.072897727 0.201723485] | [2.569829596 ¦-0.52995137 2.597460011] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
8 | 2 | [7 empty] | [0.086666667 ¦0.02907197 0.087405303] | [0.204166667 ¦0.072897727 0.201723485] | [2.569829596 ¦-0.52995137 2.597460011] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
9 | 1 | [7 empty] | [0.251742424] | [0.255208333] | [2.270366128] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
10 | 1 | [7 empty] | [0.251742424] | [0.255208333] | [2.270366128] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
11 | 1 | [7 empty] | [0.251742424] | [0.255208333] | [2.270366128] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
12 | 3 | [7 empty] | [0.288049242 ¦0.09844697 0.29032197 ¦0.093257576 0.09844697 0.288049242] | [0.142443182 ¦0.052556818 0.135643939 ¦0.040852273 0.052556818 0.142443182] | [33.77150149 ¦0 33.77150149 ¦0 0 33.77150149] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
300 | 3 | [7 empty] | [0.253181818 ¦0.039791667 0.250719697 ¦0.040340909 0.039128788 0.251780303] | [0.252708333 ¦0.109450758 0.256988636 ¦0.094981061 0.086950758 0.255132576] | [2.680150309 ¦-0.769281006 2.5610381 ¦-0.499507676 -0.312072984 2.455590387] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
301 | 3 | [7 empty] | [0.365530303 ¦0.04407197 0.36282197 ¦0.04467803 0.043333333 0.363996212] | [0.267329545 ¦0.122007576 0.270473485 ¦0.107784091 0.099204545 0.269109848] | [2.572492163 ¦-0.72160598 2.464381882 ¦-0.472329395 -0.298961096 2.368881119] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
302 | 1 | [7 empty] | [0.530208] | [0.281345] | [2.12257] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
303 | 1 | [7 empty] | [0.530208] | [0.281345] | [2.12257] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
304 | 1 | [7 empty] | [0.363958] | [0.269167] | [2.1922] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
400 | 3 | [7 empty] | [0.088205 ¦0.0312137 0.0901946 ¦0.0306264 0.0316143 0.0889665] | [0.20744 ¦0.0935314 0.200783 ¦0.0760312 0.0855879 0.204877] | [2.90301 ¦-0.679335 3.15896 ¦-0.22313 -0.481416 2.8965] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
601 | 3 | [7 empty] | [0.065625 ¦0.029545455 0.063920455 ¦0.029924242 0.02907197 0.064659091] | [0.192784091 ¦0.095018939 0.19844697 ¦0.080227273 0.072897727 0.195984848] | [3.164838036 ¦-1.002632425 2.993981593 ¦-0.632736516 -0.372608713 2.832670203] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
602 | 3 | [7 empty] | [0.142537879 ¦0.029924242 0.14157197 ¦0.029545455 0.02907197 0.140833333] | [0.22375 ¦0.080227273 0.226950758 ¦0.095018939 0.072897727 0.229393939] | [2.863013423 ¦-0.543414918 2.602031589 ¦-0.8492585 -0.330962141 2.725162768] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
603 | 2 | [7 empty] | [0.251780303 ¦0.039128788 0.250719697] | [0.255132576 ¦0.086950758 0.256988636] | [2.366017603 ¦-0.452083836 2.343963508] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
604 | 2 | [7 empty] | [0.250719697 ¦0.039128788 0.251780303] | [0.256988636 ¦0.086950758 0.255132576] | [2.343963508 ¦-0.452083836 2.366017603] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
605 | 1 | [7 empty] | [0.251742424] | [0.255208333] | [2.270366128] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
606 | 3 | [7 empty] | [0.151174242 ¦0.060454545 0.149450758 ¦0.053958333 0.060454545 0.151174242] | [0.084526515 ¦0.006212121 0.076534091 ¦-0.002708333 0.006212121 0.084526515] | [48.67459408 ¦0 48.67459408 ¦0 0 48.67459408] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
607 | 1 | [7 empty] | [0.254261364] | [0.097045455] | [44.70661522] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
721 | 3 | [7 empty] | [0.055416667 ¦0.012746212 0.050113636 ¦0.006382576 0.012746212 0.055416667] | [0.037367424 ¦-0.006969697 0.035984848 ¦-0.007897727 -0.006969697 0.037367424] | [80.27484728 ¦0 80.27484728 ¦0 0 80.27484728] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
722 | 3 | [7 empty] | [0.089981061 ¦0.030852273 0.085 ¦0.023371212 0.030852273 0.089981061] | [0.056306818 ¦-0.006174242 0.050719697 ¦-0.011496212 -0.006174242 0.056306818] | [64.2184109 ¦0 64.2184109 ¦0 0 64.2184109] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
723 | 3 | [7 empty] | [0.245 ¦0.092253788 0.246628788 ¦0.086837121 0.092253788 0.245] | [0.127140152 ¦0.039981061 0.119810606 ¦0.028806818 0.039981061 0.127140152] | [37.5977112 ¦0 37.5977112 ¦0 0 37.5977112] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
724 | 3 | [7 empty] | [0.396818182 ¦0.098560606 0.399015152 ¦0.093295455 0.098560606 0.396818182] | [0.146931818 ¦0.051856061 0.140113636 ¦0.040208333 0.051856061 0.146931818] | [30.26701029 ¦0 30.26701029 ¦0 0 30.26701029] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx601 | 3 | [6 empty] | mi | [0.3465 ¦0.156 0.3375 ¦0.158 0.1535 0.3414] | [1.0179 ¦0.5017 1.0478 ¦0.4236 0.3849 1.0348] | [2.8 ¦-0.6 2.8 ¦-0.6 -0.6 2.8] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx602 | 3 | [6 empty] | mi | [0.7526 ¦0.158 0.7475 ¦0.156 0.1535 0.7436] | [1.1814 ¦0.4236 1.1983 ¦0.5017 0.3849 1.2112] | [2.8 ¦-0.6 2.8 ¦-0.6 -0.6 2.8] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx603 | 2 | [6 empty] | mi | [1.3238 ¦0.2066 1.3294] | [1.3569 ¦0.4591 1.3471] | [2.8 ¦-0.6 2.8] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx604 | 2 | [6 empty] | mi | [1.3238 ¦0.2066 1.3294] | [1.3569 ¦0.4591 1.3471] | [2.8 ¦-0.6 2.8] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx605 | 1 | [6 empty] | mi | [1.3292] | [1.3475] | [2.8] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx606 | 3 | [6 empty] | mi | [0.791721 ¦0.318476 0.781649 ¦0.28345 0.318476 0.791721] | [0.438352 ¦0.0276838 0.396697 ¦-0.0184204 0.0276838 0.438352] | [383.948 ¦0 383.948 ¦0 0 383.948] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]
mtx607 | 1 | [6 empty] | mi | [1.3425] | [0.5124] | [236.0] | 60 | 400 | 600 | 0.1 | 20 | [8 empty] | 1 | [400.0]

## Voltagebases
Id_Voltagebases
[115.0, 4.16, 0.48]

## LoadShape
Id_LoadShape | npts | interval | mult | hour | mean | stddev | csvfile | sngfile | dblfile | action | qmult | UseActual | Pmax | Qmax | sinterval | minterval | Pbase | Qbase | Pmult | PQCSVFile | MemoryMapping | like
default | 24 | 1 | [0.677 0.6256 0.6087 0.5833 0.58028 0.6025 0.657 0.7477 0.832 0.88 0.94 0.989 0.985 0.98 0.9898 0.999 1 0.958 0.936 0.913 0.876 0.876 0.828 0.756] |  | 0.82583 | 0.15309

## GrowthShape
Id_GrowthShape | npts | year | mult | csvfile | sngfile | dblfile | like
default | 2 | [1 20] | [1.025 1.025]

## TCC_Curve
Id_TCC_Curve | npts | C_array | T_array | like
a | 5 | [1 2.5 4.5 8 14] | [0.15 0.07 0.05 0.045 0.045]
d | 5 | [1 2.5 4.5 8 14] | [6 0.7 0.2 0.06 0.02]
tlink | 7 | [2 2.1 3 4 6 22 50] | [300 100 10.1 4 1.4 0.1 0.02]
klink | 6 | [2 2.2 3 4 6 30] | [300 20 4 1.3 0.41 0.02]
uv1547 | 2 | [0.5 0.9] | [0.166 2]
ov1547 | 2 | [1.1 1.2] | [2 0.166]
mod_inv | 15 | [1.1 1.3 1.5 2 3 4 5 6 7 8 9 10 20 50 100] | [27.1053 9.9029 6.439 3.8032 2.4322 1.9458 1.6883 1.5255 1.4117 1.3267 1.2604 1.2068 0.9481 0.7468 0.6478]
very_inv | 15 | [1.1 1.3 1.5 2 3 4 5 6 7 8 9 10 20 50 100] | [93.872 28.9113 16.179 7.0277 2.9423 1.7983 1.3081 1.0513 0.8995 0.8023 0.7361 0.6891 0.5401 0.4988 0.493]
ext_inv | 15 | [1.1 1.3 1.5 2 3 4 5 6 7 8 9 10 20 50 100] | [134.407 40.9913 22.6817 9.5217 3.6467 2.0017 1.2967 0.9274 0.7092 0.5693 0.4742 0.4065 0.1924 0.133 0.1245]
definite | 3 | [1 1.001 100] | [300 1 1]

## Spectrum
Id_Spectrum | NumHarm | harmonic | %mag | angle | CSVFile | like
default | 7 | [1 3 5 7 9 11 13] | [100 33 20 14 11 9 7] | [0 0 0 0 0 0 0]
defaultload | 7 | [1 3 5 7 9 11 13] | [100 1.5 20 14 1 9 7] | [0 180 180 180 180 180 180]
defaultgen | 7 | [1 3 5 7 9 11 13] | [100 5 3 1.5 1 0.7 0.5] | [0 0 0 0 0 0 0]
defaultvsource | 1 | [1.0] | [100.0]
linear | 1 | [1.0] | [100.0]
pwm6 | 13 | [1 3 5 7 9 11 13 15 17 19 21 23 25] | [100 4.4 76.5 62.7 2.9 24.8 12.7 0.5 7.1 8.4 0.9 4.4 3.3] | [-103 -5 28 -180 -33 -59 79 36 -253 -124 3 -30 86]
dc6 | 10 | [1 3 5 7 9 11 13 15 17 19] | [100 1.2 33.6 1.6 0.4 8.7 1.2 0.3 4.5 1.3] | [-75 28 156 29 -91 49 54 148 -57 -46]

## Line
Id_Line | bus1 | bus2 | linecode | length | phases | r1 | x1 | r0 | x0 | C1 | C0 | rmatrix | xmatrix | cmatrix | Switch | Rg | Xg | rho | geometry | units | spacing | wires | EarthModel | cncables | tscables | B1 | B0 | Seasons | Ratings | LineType | normamps | emergamps | faultrate | pctperm | repair | basefreq | enabled | like
650632 | rg60.1.2.3 | 632.1.2.3 | mtx601 | 2000 | 3 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
632670 | 632.1.2.3 | 670.1.2.3 | mtx601 | 667 | 3 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
670671 | 670.1.2.3 | 671.1.2.3 | mtx601 | 1333 | 3 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
671680 | 671.1.2.3 | 680.1.2.3 | mtx601 | 1000 | 3 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
632633 | 632.1.2.3 | 633.1.2.3 | mtx602 | 500 | 3 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
632645 | 632.3.2 | 645.3.2 | mtx603 | 500 | 2 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
645646 | 645.3.2 | 646.3.2 | mtx603 | 300 | 2 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
692675 | 692.1.2.3 | 675.1.2.3 | mtx606 | 500 | 3 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
671684 | 671.1.3 | 684.1.3 | mtx604 | 300 | 2 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
684611 | 684.3 | 611.3 | mtx605 | 300 | 1 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
684652 | 684.1 | 652.1 | mtx607 | 800 | 1 | [14 empty] | ft | [7 empty] | 1 | [400.0] |  | 400 | 600
671692 | 671.1.2.3.0 | 692.1.2.3.0 |  | 0.001 | 3 | 0.0001 | 0 | 0.0001 | 0 | 0 | 0 |  |  |  | Yes

## Vsource
Id_Vsource | bus1 | basekv | pu | angle | frequency | phases | MVAsc3 | MVAsc1 | x1r1 | x0r0 | Isc3 | Isc1 | R1 | X1 | R0 | X0 | ScanType | Sequence | bus2 | Z1 | Z0 | Z2 | puZ1 | puZ0 | puZ2 | baseMVA | Yearly | Daily | Duty | Model | puZideal | spectrum | basefreq | enabled | like
source | sourcebus | 115 | 1.0001 | 30 |  |  | 20000 | 21000

## Load
Id_Load | phases | bus1 | kV | kW | kvar | kVA | pf | model | yearly | daily | duty | growth | conn | Rneut | Xneut | status | class | Vminpu | Vmaxpu | Vminnorm | Vminemerg | xfkVA | allocationfactor | %mean | %stddev | CVRwatts | CVRvars | kwh | kwhdays | Cfactor | CVRcurve | NumCust | ZIPV | %SeriesRL | RelWeight | Vlowpu | puXharm | XRharm | spectrum | basefreq | enabled | like
671 | 3 | 671.1.2.3 | 4.16 | 1155 | 660 |  |  | 1
634a | 1 | 634.1 | 0.277 | 160 | 110 |  |  | 1
634b | 1 | 634.2 | 0.277 | 120 | 90 |  |  | 1
634c | 1 | 634.3 | 0.277 | 120 | 90 |  |  | 1
645 | 1 | 645.2 | 2.4 | 170 | 125 |  |  | 1
646 | 1 | 646.2.3 | 4.16 | 230 | 132 | [7 empty] | delta
692 | 1 | 692.3.1 | 4.16 | 170 | 151 |  |  | 5 |  |  |  |  | delta
675a | 1 | 675.1 | 2.4 | 485 | 190 |  |  | 1
675b | 1 | 675.2 | 2.4 | 68 | 60 |  |  | 1
675c | 1 | 675.3 | 2.4 | 290 | 212 |  |  | 1
611 | 1 | 611.3 | 2.4 | 170 | 80 |  |  | 5
652 | 1 | 652.1 | 2.4 | 128 | 86
670a | 1 | 670.1 | 2.4 | 17 | 10 |  |  | 1
670b | 1 | 670.2 | 2.4 | 66 | 38 |  |  | 1
670c | 1 | 670.3 | 2.4 | 117 | 68 |  |  | 1

## Transformer
Id_Transformer | phases | windings | XfmrCode | buses | conns | kVs | kVAs | taps | %Rs | MaxTap | MinTap | NumTaps | normamps | emergamps | normhkVA | emerghkVA | wdg | bus | conn | kV | kVA | tap | %R | Rneut | Xneut | RdcOhms | XHL | XHT | XLT | X12 | X13 | X23 | %loadloss | %noloadloss | Xscarray | thermal | n | m | flrise | hsrise | sub | subname | %imag | ppm_antifloat | bank | XRConst | LeadLag | WdgCurrents | Core | Seasons | Ratings | faultrate | pctperm | repair | basefreq | enabled | like
sub | 3 | 2 |  | [sourcebus, 650.1.2.3.0] | [delta, wye] | [115.0, 4.16] | [5000.0, 5000.0] | [1.0, 1.0] | [0.0005, 0.0005] |  |  |  | 27.6124 | 37.6533 | 5500 | 7500 | [9 empty] | 4.9033e-06 | 0.008 | [5 empty] | 0.001 |  | [0.008]
reg1 | 1 | 2 |  | [650.1, rg60.1] | [wye, wye] | [2.4, 2.4] | [1666.0, 1666.0] | [1.0, 1.05625] | [0.005, 0.005] |  |  |  | 763.5833 | 1041.25 | 1832.6 | 2499 | [9 empty] | 0.00014694 | 0.01 | [5 empty] | 0.01 |  | [0.01]
reg2 | 1 | 2 |  | [650.2, rg60.2] | [wye, wye] | [2.4, 2.4] | [1666.0, 1666.0] | [1.0, 1.0375] | [0.005, 0.005] |  |  |  | 763.5833 | 1041.25 | 1832.6 | 2499 | [9 empty] | 0.00014694 | 0.01 | [5 empty] | 0.01 |  | [0.01]
reg3 | 1 | 2 |  | [650.3, rg60.3] | [wye, wye] | [2.4, 2.4] | [1666.0, 1666.0] | [1.0, 1.05625] | [0.005, 0.005] |  |  |  | 763.5833 | 1041.25 | 1832.6 | 2499 | [9 empty] | 0.00014694 | 0.01 | [5 empty] | 0.01 |  | [0.01]
xfm1 | 3 | 2 |  | [633.1.2.3.0, 634.1.2.3.0] | [wye, wye] | [4.16, 0.48] | [500.0, 500.0] | [1.0, 1.0] | [0.55, 0.55] |  |  |  | 76.3324 | 104.0896 | 550 | 750 | [9 empty] | 0.00071808 | 2 | [5 empty] | 1.1 |  | [2.0]

## RegControl
Id_RegControl | transformer | winding | vreg | band | ptratio | CTprim | R | X | bus | delay | reversible | revvreg | revband | revR | revX | tapdelay | debugtrace | maxtapchange | inversetime | tapwinding | vlimit | PTphase | revThreshold | revDelay | revNeutral | EventLog | RemotePTRatio | TapNum | Reset | LDC_Z | rev_Z | Cogen | basefreq | enabled | like
reg1 | reg1 | 2 | 122 | 2 | 20 | 700 | 3 | 9 |  | 15 |  | 120 | 3 |  |  | 2 |  | 16 |  | 2 |  |  | 100 | 60 |  | Yes | 20 | 9 |  |  |  |  | 60 | Yes
reg2 | reg2 | 2 | 122 | 2 | 20 | 700 | 3 | 9 |  | 15 |  | 120 | 3 |  |  | 2 |  | 16 |  | 2 |  |  | 100 | 60 |  | Yes | 20 | 6 |  |  |  |  | 60 | Yes
reg3 | reg3 | 2 | 122 | 2 | 20 | 700 | 3 | 9 |  | 15 |  | 120 | 3 |  |  | 2 |  | 16 |  | 2 |  |  | 100 | 60 |  | Yes | 20 | 9 |  |  |  |  | 60 | Yes

## Capacitor
Id_Capacitor | bus1 | bus2 | phases | kvar | kv | conn | cmatrix | cuf | R | XL | Harm | Numsteps | states | normamps | emergamps | faultrate | pctperm | repair | basefreq | enabled | like
cap1 | 675.1.2.3.0 | 675.1.2.3.0.0.0 | 3 | [600.0] | 4.16 | wye | [0 ¦1.87639338887875E-310 2.25607960651843E-308 ¦9.21786364221574E-306 0 9.21786786141778E-306] | [91.9673] |  |  |  | 1 | [1.0] | 112.4168 | 149.889 | 0.0005 | 100 | 3 | 60 | Yes
cap2 | 611.3 | 611.0.0.0 | 1 | [100.0] | 2.4 | wye |  | [46.0518] |  |  |  | 1 | [1.0] | 56.25 | 75 | 0.0005 | 100 | 3 | 60 | Yes